TENon® Self-Regulating Heating Cables

|  | Field of Use: Self-Regulating Heating Cable of TENon® trademark is used in various branches of industry: in oil-and-gas, chemical, fuel, metallurgic, and others. It is designed for protection against freezing and for maintaining the process temperature of surfaces of pipes, tanks and vessels, as well as for protection of roof and drain system components against the formation of frost. Description of the Cable: TU 16.K180-080-2019 Standard Cable Brand Name of cable components Fire Hazard Class KSENt(f) Self-Regulating Heating Cable low-temperature О1.8.2.5.4 KSESf Self-Regulating Heating Cable medium-temperature О1.8.2.5.4 KSEVf Self-Regulating Heating Cable high-temperature О1.8.2.5.4 t – sheath of thermoplastic elastomer f – sheath of PTFE |
| --- | --- |

- Technical Characteristics:

| TENon® Cable Brand | Cable Specific Capacity at 10°С, W/m | T Class | t max in Operating State, °С | t max in Idle State, °С | Explosion Proof Marking |
| --- | --- | --- | --- | --- | --- |
| KSENt(f) | 10/15/25/33 | Т6 | + 65 | + 85 | 1Ех c IIС Т6 Gb Х |
| KSESf | 10/15/25/30/ 45/60 | Т3 | + 120 | + 200 | 1Ех c IIС Т3 Gb Х |
| KSEVf | 15/30/45/ 60/75/90 | Т2 | + 200 | + 250 | 1Ех c IIС Т2 Gb Х |

TENon® – KSEN Low-Temperature Heating Cable

|  | Design: 1. Copper tinned or nickel-clad conductors of 2х1.2 mm2 cross-section. * 2. Semi-conducting self-regulating matrix. 3. Insulation with properties corresponding to the outer sheath. 4. Braid of copper tinned wires. 5. Sheath of thermoplastic elastomer (t), PTFE (f). ** * another conductor cross-section is allowed (≥ 1.2 mm2) ** manufacture of cable with other sheaths is allowed Field of Use: Protection against freezing of pipes, tanks and vessels which are not subjected to steam treatment. Technical Characteristics: Heat generation power at 10° 10/15/25/33 W/m Maximum operation temperature + 65°С Max. permissible temperature without load + 85°С Nominal voltage 230 V Protection degree IP 66 Temperature class Т6 Explosion proof marking 1Ех c IIС Т6 Gb Х Features: |
| --- | --- |

- Specific released power at a cable section depends on the ambient temperature.

- The cable can be cut to any necessary length on site.

- The cable can be installed at negative ambient temperatures.

- It is possible to use it in safe and explosion hazard zones of Classes 1 and 2 according to GOST 30852.13.

- PTFE sheath is resistant to the effects of chemical aggressive environments, as well as to climatic effects, including negative temperatures down to - 60°С.

- Ordering Information:

TENon-KSENt-10 W/m Т6 0.22 kV TU 16.K180-080-2019

Cable type: KSEN

Sheath material: t – thermoplastic elastomer

Linear heat generation rate: 10 W/m

TENon® – KSEN Power Characteristics

Maximum Cable Length (m) When Using C-Type Automatic Circuit Breaker

| Type of Automatic Circuit Breaker | cut-in t, °С | KSEN-10 | KSEN-15 | KSEN-25 | KSEN-33 |
| --- | --- | --- | --- | --- | --- |
| 16 А | +10 | 205 | 145 | 88 | 70 |
|  | -15 | 139 | 93 | 58 | 49 |
|  | -30 | 120 | 77 | 45 | 43 |
| 20 А | +10 | 205 | 162 | 117 | 90 |
|  | -15 | 186 | 125 | 75 | 64 |
|  | -30 | 150 | 106 | 64 | 52 |
| 25 А | +10 | 205 | 162 | 120 | 98 |
|  | -15 | 190 | 142 | 95 | 80 |
|  | -30 | 170 | 135 | 82 | 65 |
| 32 А | +10 | 205 | 162 | 126 | 108 |
|  | -15 | 195 | 160 | 117 | 95 |
|  | -30 | 195 | 160 | 100 | 82 |

TENon® KSES Middle-Temperature Heating Cable

|  | Design: 1. Copper tinned or nickel-clad conductors of 2х1.2 mm2 cross-section. * 2. Semi-conducting self-regulating matrix. 3. Insulation with properties corresponding to the outer sheath. 4. Braid of copper tinned wires. 5. Sheath from fluoroplastic (f). ** * another conductor cross-section is allowed (≥ 1.2 mm2) ** manufacture of cable with other sheaths is allowed Field of Use: Protection against freezing of pipes, tanks and vessels which are subjected to steam treatment. Technical Characteristics: Heat generation power at 10°С 10/15/25/30/45/60 W/m Maximum operation temperature + 120°С Max. permissible temperature without load + 200°С Nominal voltage 230 V Protection degree IP 66 Temperature class Т3 Explosion proof marking 1Ех c IIС Т3 Gb Х Features: |
| --- | --- |

- Specific released power at a cable section depends on the ambient temperature.

- The cable can be cut to any necessary length on site.

- The cable can be installed at negative ambient temperatures.

- It is possible to use it in safe and explosion hazard zones of Classes 1 and 2 according to GOST 30852.13.

- PTFE sheath is resistant to the effects of chemical aggressive environments, as well as to climatic affects, including negative temperatures down to - 60°С.

- Ordering Information:

TENon-KSESf-45 W/m Т3 0.22 kV  TU 16.K180-080-2019

Cable type: KSES

Sheath material: f – PTFE

Linear heat generation rate: 45 W/m

TENon® – KSES Power Characteristics

Maximum Cable Length (m) When Using C-Type Automatic Circuit Breaker

| Type of Automatic Circuit Breaker | cut-in t, °С | KSES-10 | KSES-15 | KSES-25 | KSES-30 | KSES-45 | KSES-60 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 16 А | +10 | 200 | 165 | 120 | 85 | 70 | 50 |
|  | -15 | 175 | 117 | 88 | 69 | 49 | 38 |
|  | -30 | 165 | 110 | 80 | 65 | 45 | 35 |
| 20 А | +10 | 235 | 189 | 140 | 114 | 82 | 64 |
|  | -15 | 235 | 152 | 120 | 92 | 66 | 52 |
|  | -30 | 225 | 144 | 114 | 86 | 62 | 48 |
| 25 А | +10 | 235 | 189 | 140 | 114 | 82 | 64 |
|  | -15 | 235 | 170 | 130 | 100 | 75 | 58 |
|  | -30 | 230 | 160 | 120 | 92 | 70 | 52 |
| 32 А | +10 | 235 | 189 | 140 | 114 | 82 | 64 |
|  | -15 | 235 | 189 | 140 | 114 | 82 | 64 |
|  | -30 | 235 | 189 | 136 | 110 | 78 | 60 |

TENon® – KSEV High-Temperature Heating Cable

|  | Design: 1. Copper tinned or nickel-clad conductors of 2х1.2 mm2 cross-section. * 2. Semi-conducting self-regulating matrix. 3. Insulation with properties corresponding to the outer sheath. 4. Braid of copper tinned wires. 5. Sheath of PTFE (f). ** * another conductor cross-section is allowed (≥ 1.2 mm2) ** manufacture of cable with other sheaths is allowed Field of Use: Protection against freezing or for maintaining a set technology temperature of pipes and tanks and other process equipment, as well as in systems with high temperature exposure of the heating cable. Technical Characteristics: Heat generation power at 10°С 15/30/45/60/75/90 W/m Maximum operation temperature + 200°С Max. permissible temperature without load + 250°С Nominal voltage 230 V Protection degree IP 66 Temperature class Т2 Explosion proof marking 1Ех c IIС Т2 Gb Х Features: |
| --- | --- |

- Specific released power at a cable section depends on the ambient temperature.

- The cable can be cut to any necessary length on site.

- The cable can be installed at negative ambient temperatures.

- It is possible to use it in safe and explosion hazard zones of Classes 1 and 2 according to GOST 30852.13.

- PTFE sheath is resistant to the effects of chemical aggressive environments, as well as to climatic affects, including negative temperatures down to - 60°С.

- Ordering Information:

TENon-KSEVf-60 W/m Т2 0.22 kV  TU 16.K180-080-2019

Cable type: KSEV

Sheath material: f – PTFE

Linear heat generation rate: 60 W/m

TENon® – KSEV Power Characteristics

Maximum Cable Length (m) When Using C-Type Automatic Circuit Breaker

| Type of Automatic Circuit Breaker | cut-in t, °С | KSEV-15 | KSEV-30 | KSEV-45 | KSEV-60 | KSEV-75 | KSEV-90 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 6 А | +10 | 48 | 30 | 24 | 18 | 16 | 12 |
|  | 0 | 46 | 30 | 22 | 18 | 14 | 12 |
|  | -20 | 40 | 26 | 20 | 16 | 14 | 10 |
| 10 А | +10 | 78 | 52 | 38 | 30 | 26 | 22 |
|  | 0 | 76 | 48 | 36 | 30 | 24 | 20 |
|  | -20 | 68 | 44 | 34 | 26 | 22 | 18 |
| 16 А | +10 | 126 | 82 | 62 | 50 | 42 | 36 |
|  | 0 | 120 | 78 | 58 | 46 | 40 | 32 |
|  | -20 | 108 | 70 | 52 | 42 | 36 | 30 |
| 20 А | +10 | 154 | 102 | 78 | 62 | 52 | 42 |
|  | 0 | 150 | 96 | 74 | 58 | 48 | 40 |
|  | -20 | 136 | 88 | 66 | 52 | 44 | 36 |
| 25 А | +10 | - | 108 | 88 | 76 | 64 | 54 |
|  | 0 | 154 | 108 | 88 | 72 | 60 | 50 |
|  | -20 | 154 | 108 | 82 | 66 | 54 | 46 |
| 32 А | +10 | - | - | 88 | 76 | 82 | 68 |
|  | 0 | - | - | 88 | 76 | 78 | 64 |
|  | -20 | - | - | 88 | 76 | 70 | 58 |

# Text boxes

KSEN 33

KSEN 25

KSEN 15

KSEN 10

Pipe Temperature [°C]

Heat Power [W/m]

KSES 10

Pipe Temperature [°C]

KSES 60

KSES 40

KSES 30

KSES 25

KSES 15

Heat Power [W/m]

KSEN 90

KSEV 75

KSEV 60

KSEV 45

KSEV 30

KSEV 15

Pipe Temperature [°C]

Heat Power [W/m]